## Data Sheet
TWEED SHIRE COUNCIL | Data Sheet
Project:
Item |  | Grit Pump
Tag Numbers
Qty Required
Location
Item | Units | Requirement | Offer
Grit Pumps
Item | Units | Requirement | Offer
Location | - | 0
Tag Number | - | 0
Quantity Required | No.
VENDOR INFORMATION
Type |  | Recessed Impeller Centrifugal/Self Priming
Make | - | Supplier Advise
Model | -
Manufacturer | -
DESIGN LIFE
Years (before equipment replacement) | Years | 25
Duty configuration | - | Duty / Standby
OPERATING CONDITION
Ambient Environment | - | Inland/coastal aggressive
Ambient Temperature Range (oC) | oC | 0-400 C
Fluid | - | Grit Slurry
Fluid Temperature Range | oC | 15-35 0C
Humidity | % | 20-100
Fluid pH Range | pH | 5 to 9
Fluid Specific Density | kg/m3 | 950 - 1200 (Approx)
Project Site Elevation | mAHD | -
Total Suspended Solids | mg/L | TBA
PERFORMANCE
Vibration Monitoring | - | Required on rotating equipment larger than 10 kW
Duty Flow Rate | L/s
Duty Head | m
System Curve / Pump Curve |  | System Curve avaliable
Approximate NSPHa | m | N / A
NPSHr | kPa(g) | Supplier Advise
Pump Speed | RPM | Supplier Advise
Mounting |  | Dry Mounted
Priming |  | N/A Flooded suction
TESTING |  | Pump with more than 15 KW capacity to be tested in accordance with AS2417.2 (Pumps Hydraulic Performance Acceptance test), AS1359.109 (Noise Limits), AS1359.114 (vibration measurements and limits test) and AS1359.101 (Motor Type Test).
DIMENSIONS
Suction Size | DN | Supplier Advise
Suction Connection (flange type) | - | Supplier Advise
Discharge Size | DN | Supplier Advise
Discharge Connection (flange type) | - | Supplier Advise
Overall Height | mm | Supplier Advise
Overall Width | mm | Supplier Advise
Overall Length | mm | Supplier Advise
Impeller | mm | Supplier Advise
MATERIALS
Body |  | Supplier Advise
Volute |  | Supplier Advise
Impeller | - | Supplier Advise
Wear Rings | - | Supplier Advise
Shaft | - | Supplier Advise
Seals | - | Supplier Advise
Casing | - | Supplier Advise
Fasteners | - | AISI 316
Guiderails | - | 316 Stainless Steel
OTHER
Pump shall be able to withstand a closed valve / no flow head.
WEIGHTS
Total Weight (dry) | kg | Supplier Advise
DRIVE MOTOR
Make |  | Supplier Advise
IP Rating |  | 56
Frame |  | Supplier Advise
Power | kW | Supplier Advise
Speed | RPM | 1500 (Max)
Voltage | V | 415
Phase | No. | Three
Frequency | Hz | 50
Suitable for VSD | - | No
Method of Mechanical overload Protection | - | Supplier Advise
Thermisters | - | Required for Drives Larger than 5.5 kW
Motor Cooling |  | Ambient Air
SPEED REDUCTION
Drive Detail (Direct / Belt / Chain / Gearbox) | - | Direct Drive
Type and Number of Stages | - | N/A
Manufacturer | - | N/A
Service Factor | - | N/A
Final Drive Ratio | - | N/A
COUPLING
Coupling Type |  | Supplier Advise
OPERATIONAL NOISE
Sound Power Level at 1m | DbA | Supplier Advise
HAZARDOUS AREA RATING
Classification | - | Non Hazardous
PROTECTIVE COATINGS
Pump |  | Epoxy enamel
Motor coating( if applicable) |  | Epoxy enamel
EQUIPMENT LABELING
Label Material |  | SS316
Information Required |  | TBA
Fixing Method |  | TBA
Lubrication Label |  | TBA
DOCUMENTATION
Drawings |  | AutoCAD - General arrangements with offer
Pump and efficiency curves |  | To be supplied with offer
Operation and Maintenance Manuals |  | TBA
SPARE PARTS
Recommended Spares |  | Supplier Advise
Availability |  | Supplier Advise
Warehouse location |  | Supplier Advise
Pricing |  | Provide as seperable schedule
SPECIFICATIONS INCLUDE |  | ME01, ME02
DOCUMENT STATUS
Revision:
Prepared by:
Mechanical checked by:
Electrical checked by:
Process checked by:
Approved by: