## Data Sheet
TWEED SHIRE COUNCIL | Data Sheet
Project:
Item |  | Progressive Cavity/Rotary Lobe Pump
Tag Numbers
Qty Required
Location
Item | Units | Requirement | Offer
Progressive Cavity or Rotary Lobe Pump
Location | - | 0
Tag Number | -
Quantity Required | No.
VENDOR INFORMATION
Type |  | Progressive Cavity
Make | - | Supplier Advise
Model | -
Manufacturer | - | Supplier Advise
DESIGN LIFE
Years (before equipment replacement) | Years | 25
Duty configuration | - | Duty / Duty
OPERATING CONDITION
Ambient Environment | - | Inland/Coastal Aggressive
Ambient Temperature Range (oC) | oC | 0-400 C
Fluid | -
Fluid Temperature Range | oC | 10-35 0C
Humidity | % | 20-100
Fluid pH Range | pH
Fluid Specific Density | kg/m3
Fluid Absolute Viscosity | mPas
Project Site Elevation | m
Diameter of solid sphere required to be passed | mm
Rag Content | %
Maximum Solids Content | %
PERFORMANCE
Vibration Monitoring | - | Required on rotating equipment larger than 10 kW
Duty Flow Rate | L/s
Duty Head | m
Approximate NSPHa | m
NPSHr | kPa(g) | N/A
Pump Speed | RPM | Supplier Advise
Priming |  | N/A
Turn Down |  | N/A
Max Pump Set Noise Level at 1 m | dBA(1m) | <75
TESTING |  | Pump with more than 15 KW capacity to be tested in accordance with AS2417.2 (Pumps Hydraulic Performance Acceptance test), AS1359.109 (Noise Limits), AS1359.114 (vibration measurements and limits test) and AS1359.101 (Motor Type Test).
DIMENSIONS
Suction Size | DN | N/A
Suction Connection | - | N/A
Discharge Size | DN | Supplier Advise
Discharge Connection | -
Overall Height | mm | Supplier Advise
Overall Width | mm | Supplier Advise
Overall Length | mm | Supplier Advise
Impeller | mm | Supplier Advise
Length of Guiderails | m | N/A
Length of Power and controls cable | mm | Supplier Advise
MATERIALS
Body/casing |  | Supplier Advise
Stator |  | Supplier Advise
Rotor/Lobes | - | Supplier Advise
Shaft | - | Supplier Advise
Seals | - | Supplier Advise
Baseplate | - | Galvanised Steel
Fasteners | - | AISI 316
OTHER
WEIGHTS
Total Weight (dry) | kg | Supplier Advise
DRIVE MOTOR
Make |  | Supplier Advise
IP Rating |  | 56
Frame |  | Supplier Advise
Power | kW | Supplier Advise
Speed | RPM | 1500 (Max)
Voltage | V | 415
Phase | No. | Three
Frequency | Hz | 50
Suitable for VSD | - | No
Method of Mechanical overload Protection | - | Supplier Advise
Thermisters | - | Required for Drives Larger than 5.5 kW
SPEED REDUCTION
Drive Detail (Direct / Belt / Chain / Gearbox) | - | Gearbox
Type and Number of Stages | - | N/A
Manufacturer | - | N/A
Service Factor | - | N/A
Final Drive Ratio | - | N/A
COUPLING
Coupling Type |  | Supplier Advise
OPERATIONAL NOISE
Sound Power Level at 1m | - | Supplier Advise
HAZARDOUS AREA RATING
Classification | - | Non Hazardous
PROTECTIVE COATINGS
Requirements |  | Epoxy enamel
Motor coating( if applicable) |  | Epoxy enamel
EQUIPMENT LABELING
Label Material |  | SS316
Information Required |  | TBA
Fixing Method |  | TBA
Lubrication Label |  | TBA
DOCUMENTATION
Drawings |  | AutoCAD - General arrangements with offer
Operation and Maintenance Manuals |  | TBA
SPARE PARTS
Recommended Spares |  | Please List
Availability |  | Advise
Warehouse location |  | Advise
Pricing |  | Provide as seperable schedule
SPECIFICATIONS INCLUDE |  | ME01, ME02
DOCUMENT STATUS
Revision:
Prepared by:
Mechanical checked by:
Electrical checked by:
Process checked by:
Approved by: