## Sheet1
TWEED SHIRE COUNCIL | Data Sheet
Project:
Item |  | Storage Tank
Tag Numbers
Qty Required
Item | Units | Requirement | Offer
STORAGE TANK
Make | - | Supplier Advise
Model | - | Supplier Advise
Manufacturer | - | Supplier Advise
DESIGN LIFE
Years (before equipment replacement) | Years | 15-25
Duty | - | Continuous
OPERATING CONDITION
Ambient Environment | - | Inland/Coastal Aggressive
Ambient Temperature Range | oC | 10 to 30
Fluid | - | ?% Contents name
Fluid Temperature Range | oC | ?
Fluid pH Range | pH | ?
Fluid Specific Gravity | kg/m3 | ?
Fluid Absolute Viscosity | cps | ?
Project Site Elevation | m | ? AHD
DESIGN
Geometry | - | Vertical Cylindrical. Closed and Dished Cover Flat Bottom
Capacity (Working) | L | ?
Materials | - | FRP with Suitable Liner/steel/polypropylene
DIMENSIONS
Diameter | mm | Supplier Advise
Wall Height | mm | Supplier Advise
Overall Height | mm | Supplier Advise
Tank Cover Thickness | mm | Supplier Advise
Top and bottom cover knuckle radius | mm | Minimum 40 mm
Minimum Tank Base Thickness | mm | 8 mm
FITTINGS
Outlet | mm | ? NB AS2129 Table D
Inlet | mm | ? NB AS2129 Table D
Drain | mm | ? NB AS2129 Table D
Overflow | mm | ? NB AS2129 Table D
Level 1 | mm | ? NB AS2129 Table D
Level 2 | mm | ? NB AS2129 Table D
Level 3 | mm | ? NB AS2129 Table D
Level 4 | mm | ? NB AS2129 Table D
Spare | mm | ? NB AS2129 Table D
Vent |  | ? NB with Insect Mesh
Access |  | 800 Diameter in Tank Cover 600 Wide Non-Slip Surface Surrounding cover and 800 Diameter in side near base
Lifting Lugs | - | 2/4 Required
Anchor Feet | - | 4 Required
Flange Projection | mm | 150 from tank wall. Off Centre Drilling
Nameplate Bracket |  | 150 mm high lettering all in FRP
Gasket Material |  | EPDM OR Viton
OTHER: |  | Tank cover to be capable of supporting the weight of maintenance personell
All flanges are to be supplied with suitable gaskets and AISI 316 fasteners
Nozzles on tank top cover shall consist of 6 mm minimum thickness plate gussets laminated to the nozzle and tank top cover.
Tank shall be designed to allow complete desludging.
TESTING: |  | Hydrostatic to 2m water column in excess of normal pressure when full
WEIGHTS
Total Weight (dry) | kg | Supplier Advise
PROTECTIVE COATINGS
Requirements |  | Gel Coat Suited to Material Contained/other coating as specified
Colour |  | TBA
EQUIPMENT LABELING
Label Material |  | SS316
Information Required |  | To specification
Fixing Method |  | To specification
DOCUMENTATION
Drawings |  | AutoCAD - General arrangements with offer
Operation and Maintenance Manuals |  | To Specification
SPARE PARTS
Reccommended Spares |  | Please List
Availability |  | Advise
Warehouse location |  | Advise
Pricing |  | Provide as seperable schedule
SPECIFICATIONS INCLUDE |  | ME01
DOCUMENT STATUS
Revision:
Prepared by:
Mechanical checked by:
Electrical checked by:
Process checked by:
Approved by: