## Sheet1
TWEED SHIRE COUNCIL | Data Sheet
Project:
Item |  | Submersible pump
Tag Numbers
Qty Required
Location
Item | Units | Requirement | Offer
SUBMERSIBLE PUMP
Location | - | 0
Tag Number | - | 0
Quantity Required | No. | 0
VENDOR INFORMATION
Type |  | Submersible Centrifugal Pump to comply with WSAA/WSA101
Make | - | Supplier Advise
Model | -
Manufacturer | -
DESIGN LIFE
Years (before equipment replacement) | Years | 25
Duty configuration | - | Duty
OPERATING CONDITION
Ambient Environment | - | Inland/Coastal
Ambient Temperature Range (oC) | oC | 0-300 C
Fluid | - | Effluent
Fluid Temperature Range | oC | 15-35 0C
Fluid pH Range | pH | 5 to 9
Fluid Specific Density | kg/m3 | 1000
Fluid Absolute Viscosity | mPas | 1
Project Site Elevation | mAHD
Total Suspended Solids | mg/L | 5 to 30
PERFORMANCE
Vibration Monitoring | - | Required on rotating equipment larger than 10 kW
Duty Flow Rate | L/s
Duty Head | m
Approximate NSPHa | m
NPSHr | kPa(g) | Supplier Advise
Pump Speed | RPM | Supplier Advise
Motor Cooling |  | Cooling Jacket/Supplier Advise
TESTING |  | Pump with more than 15 KW capacity to be tested in accordance with AS2417.2 (Pumps Hydraulic Performance Acceptance test), AS1359.109 (Noise Limits), AS1359.114 (vibration measurements and limits test) and AS1359.101 (Motor Type Test).
DIMENSIONS
Suction Size | DN
Suction Connection | - | Supplier Advise
Discharge Size | DN | ?mm Preferred - Supplier Advise
Discharge Connection | - | PN16 standard flanged
Overall Height | mm | Supplier Advise
Overall Width | mm | Supplier Advise
Overall Length | mm | Supplier Advise
Impeller | mm | Supplier Advise
Length of Guiderails | mm | ?
Length of Power and controls cable | mm | Supplier Advise
MATERIALS
Body |  | Supplier Advise
Volute |  | Supplier Advise
Impeller | - | Supplier Advise
Wear Rings | - | Supplier Advise
Shaft | - | Supplier Advise
Seals | - | Supplier Advise
Casing | - | Supplier Advise
Duckfoot Bend | - | Supplier Advise
Fasteners | - | AISI 316
Motor end bells(if applicable) | - | Supplier Advise
Guiderails | - | 316 Stainless Steel
OTHER
Pump shall be able to withstand a closed valve / no flow head.
Pump shall include a duckfoot bend adaptor.
WEIGHTS
Total Weight (dry) | kg | Supplier Advise
DRIVE MOTOR
Make |  | Supplier Advise
IP Rating |  | 66
Frame |  | Supplier Advise
Power | kW | Supplier Advise
Speed | RPM | 1500 (Max)
Voltage | V | 415
Phase | No. | Three
Frequency | Hz | 50
Suitable for VSD | - | Yes
Method of Mechanical overload Protection | - | Supplier Advise
Thermisters | - | Required for Drives Larger than 5.5 kW
SPEED REDUCTION
Drive Detail (Direct / Belt / Chain / Gearbox) | - | Direct Online
Type and Number of Stages | - | N/A
Manufacturer | - | N/A
Service Factor | - | N/A
Final Drive Ratio | - | N/A
COUPLING
Coupling Type |  | Supplier Advise
OPERATIONAL NOISE
Sound Power Level at 1m | - | Supplier Advise
HAZARDOUS AREA RATING
Classification | - | Non Hazardous
PROTECTIVE COATINGS
Requirements |  | To specification
Motor coating( if applicable) |  | Epoxy enamel
EQUIPMENT LABELING
Label Material |  | SS316
Information Required |  | To specification
Fixing Method |  | To specification
Lubrication Label |  | To specification
DOCUMENTATION
Drawings |  | AutoCAD - General arrangements with offer
Operation and Maintenance Manuals |  | To Specification
SPARE PARTS
Recommended Spares |  | Please List
Availability |  | Advise
Warehouse location |  | Advise
Pricing |  | Provide as seperable schedule
SPECIFICATIONS INCLUDE |  | ME01, ME02
DOCUMENT STATUS
Revision:
Prepared by:
Mechanical checked by:
Electrical checked by:
Process checked by:
Approved by: