## Valve Schedule
TWEED SHIRE COUNCIL
Project:
Title: |  | VALVE SCHEDULE
Document No:
Rev No.
Tag prefix | Tag No. | Description | Fluid | DN | Disc/gate Material | Type | Actuator | Connection | Rating | Working Pressure | P&ID # | Body | Seat/Seal | Ext. Spindle length | Position of actuated valves after power failure | Price | Specification | Comments | Height from centre line to top of actuator. | Overall length | Weight
Inlet Works
VLV | 23110 | Grit Transfer Pipework Bottom Isolation Valve | Fluidised Grit & Sewerage | 125 |  | Gate | Manual Handwheel | Double Flanged to AS4087-2005 | PN16 Minimum |  | STW-64/M-012 | Cast Iron to AS 1830 |  |  |  |  | ME04 | This valve must be lockable
VLV | 23293 | Grit Transfer pipework Top Air Scour/lockable line clearing Valve | Compressed Air | 50 | Cast iron/ductile iron/stainless steel | Ball | Manual Lever | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | 316 Stainless Steel | Natural/Synthetic Rubber |  |  |  | ME04 | This valve must be lockable
VLV | 23292 | Compressor Receiver Inlet Isolation Valve | Compressed Air | 50 | Cast iron/ductile iron/stainless steel | Ball | Manual Lever | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | 316 Stainless Steel | Natural/Synthetic Rubber |  |  |  | ME04
RV | 23291 | Compressor Non Return Valve | Compressed Air | 50 | Bronze | Swing Check | Self Actuated | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | Bronze to AS1628 |  | Yes |  |  | ME04
PRV | 23293 | Receiver Pressure Relief Valve | Compressed Air | 40 |  | Self Actuated Spring | Self Actuated | BSP Thread Screw Connection | 900KPa |  | STW-64/M-012 | Bronze |  |  |  |  | ME04
PCV | 23290 | Pressure Control Valve-air | Compressed Air | 50 | neoprene | Spring self operated pressure regulator | Spigot End | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | Bronze |  |  |  |  | ME04
FCV | 23290 | Flow Control Valve - air | Compressed Air | 50 |  | Eccentric Plug | Electric | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | 316 Stainless Steel |  |  |  |  | ME04
- | - | Pressure Indicator Isolation Valve | Compressed Air | 15 | Cast iron/ductile iron/stainless steel | Ball Valve | Manual Lever | BSP Thread Screw Connection | PN10 Minimum |  | STW-64/M-012 | 316 Stainless Steel | Natural/Synthetic Rubber |  |  |  | ME04
- | - | Air Receiver Drain Valve |  | 25 |  | Automatic Solenoid Valve | Automatic | BSP Thread Screw Connection | PN10 Minimum |  | STW-64/M-012 | [5 empty] | ME04
RV | 23295 | Grit Removal New Air Supply Non Return Valve | Compressed Air | 50 | Bronze | Swing Check Valve | Self Actuated | BSP Thread Screw Connection | PN16 Minimum |  | STW-64/M-012 | Bronze |  | Yes |  |  | ME04
VLV | 2354 | Supernatant Return Pump 1 Isolation | Supernatant | 150 |  | Gate check | Manual Handwheel | Double Flanged to AS4087-2004 | PN10 Minimum |  | STW-64/M-012 | Cast Iron to AS 1830 |  |  |  |  | ME04
RV | 2355 | Supernatant Return Pump 1 Non Return. | Supernatant | 150 |  | Swing Check | Self Actuated counter-balanced swing gate type | Double Flanged to AS4087-2005 | PN10 Minimum |  | STW-64/M-012 | Cast Iron to AS 3578 |  |  |  |  | ME04
SBR
VLV | 435H | Pump 1 RAS Line isolation - SBR Basin 1 | Returned Activated Sludge | 150 | 316 Stainless Steel | Knife Gate | Manual Handwheel | Double Flanged to AS4087-2007 | PN10 Minimum |  |  | SG iron | Resilient |  |  |  | ME04
VLV | 434E | Pump 16 RAS Line isolation - SBR Basin 4 | Returned Activated Sludge | 150 | 316 Stainless Steel | Knife Gate | Manual Handwheel | Double Flanged to AS4087-2007 | PN10 Minimum |  |  | SG iron | Resilient |  |  |  | ME04
- | - | 2 x Line clearing compressed air valve - SBR Basin 1 | Compressed Air | 50 | Cast iron/ductile iron/stainless steel | Ball | Manual Lever | BSP Thread Screw Connection | PN10 Minimum |  |  | 316 Stainless Steel | Natural/Synthetic Rubber |  |  |  | ME04
- | - | 2 x Line clearing compressed air valve - SBR Basin 4 | Compressed Air | 50 | Cast iron/ductile iron/stainless steel | Ball | Manual Lever | BSP Thread Screw Connection | PN10 Minimum |  |  | 316 Stainless Steel | Natural/Synthetic Rubber |  |  |  | ME04
Equalisation Basin
RV | 73041 | Filter Feed Pump 3 Non Return Valve | Process Water | 450 |  | Swing Check | Self Actuated | Double Flanged to AS4087-2007 | PN10 Minimum |  |  | Cast Iron to AS 3578 |  |  |  |  | ME04
VLV | 73042 | Filter Feed Pump 3 Isolation Valve | Process Water | 450 | Cast iron/ductile iron/stainless steel | Butterfly | Spigot End | Double Flanged to AS4087-2007 | PN10 Minimum Class 150B |  |  | Cast Iron to AS 1830 | Rubber to AWWA C504 |  |  |  | ME04
VLV | 72150 | Filter Feed Actuated Bleed Valve | Process Water | 150 | SG Iron | Plug | Manual Lever | Double Flanged to AS4087-2007 | PN10 Minimum |  |  | SG Iron |  |  |  |  | ME04

## Penstocks
TWEED SHIRE COUNCIL
Project:
Title: |  | PENSTOCK AND STOPBOARD SCHEDULE
Document No:
Rev:
Revision Date
Tag prefix | Tag No. | Description | Medium | Size (HxW) or DIA. | Material | Type | Cast in or Flush Mounted | Actuator type | Rating | On seating or off seating | Upstream Pressure on penstock when closed | Downstream Pressure on penstock when closed | P&ID # | Ext. Spindle length | Price | Specification | Comments | Maximum Vertical Dim. | Maximum Horizontal Dim. | Weight
PEN | 83510 | New Contact Tank Isolation Penstock | Chlorinated Process Water | 1880 x 1500 | 316 Stainless Steel | In channel | Cast in | Electric |  | Off seating | 3 metres | nil |  | 1 metre
PEN | 83520 | Clarifier Outlet Penstock | Treated Effluent | 1000 dia | 316 Stainless Steel | Wall mounted | Flush Mounted | Manual |  | On seating | 2 metres | 2 metres |  | nil
SBD | 1234 | Inlet Channel isolation | Sewage | 2100 x 2100 | Aluminium | In channel | Cast in | N/A |  | On seating | 2 metres | 0 metres |  | nil